100Gbps QSFP28 直连高速线缆

描述 ：

100G QSFP28直连高速线缆产品，基于4X25G或4X28G结构，该产品可以满足下一代100G交换机，服务器，路由器等产品应用的需求。

QSFP28电缆组件采用优化设计来减少串扰和插入损耗，提供极好的信号完整性，并完全符合下一代100G以太网和无限带宽 EDR标准。

1.1 产品特点

• 增强了EMI / EMC性能

• 每个通道25Gbps的数据传输速率，高达100Gbps

• 符合IEEE 802.3bj标准和Infiniband EDR规范

• 符合QSFP + MSA和SFF-8661 / SFF-8665标准

• 通过EEPROM支持串行ID功能

• 提供30AWG至26AWG电缆

• RoHS和无卤素选项

1.2 应用 :

• 交换机/路由器/ HBA / SAN，NIC卡

• 40G \ 100G以太网

• 存储，交换机，数据中心，网络中心

• 无限带宽, QDR / EDR.

1.3 轮廓图:

1.4接线图：

2电气性能：

2.1 信号完整性

| 项目 | 需求 | 测试条件 |
| --- | --- | --- |
| Differential Impedance | Cable Impedance | 105+5/-10Ω | Rise time of 25ps (20 % - 80 %). |
|  | Paddle Card Impedance | 100±10Ω |  |
|  | Cable Termination Impedance | 100±15Ω |  |
| Differential (Input/Output)Return loss SDD11/SDD22 | Return_loss(f)≥ Where f is the frequency in GHz Return loss(f) is the return loss at frequency f | 10MHz≤f ≤19GHz |
| Differential to common-mode (Input/Output)Return loss SCD11/SCD22 | Return_loss(f)≥ Where f is the frequency in GHz Return_loss(f) is the Differential to common-mode return loss at frequency f | 10MHz≤f ≤19GHz |
| Common-mode to Common-mode (Input/Output)Return loss SCC11/SCC22 | Return_loss(f)≥2dB 0.2≤f≤19 Where is the frequency in GHz Return_loss(f) is the common-mode to common-mode return loss at frequency f | 10MHz≤f ≤19GHz |
| Differential Insertion Loss (SDD21 Max.) | (Differential InsertionLoss Max. For TPa to TPb Excluding Test fixture ) | 10MHz≤f ≤19GHz |
|  | F AWG | 1.25GHz | 2.5GHz | 5.0GHz | 7.0GHz | 10Ghz | 12.89Ghz |  |
|  | 30(1m)Max. | 4.5dB | 5.4dB | 6.3dB | 7.5dB | 8.5dB | 10.5dB |  |
|  | 30/28(3m)Max. | 7.5dB | 9.5dB | 12.2dB | 14.8dB | 18.0dB | 21.5dB |  |
|  | 26(3m)Max. | 5.7dB | 7.2dB | 9.9 dB | 11.9dB | 14.1dB | 16.5dB |  |
|  | 26/25(5m)Max. | 7.8dB | 10.0dB | 13.5dB | 16.0dB | 19.0dB | 22.0dB |  |
| Insertion Loss Deviation | -0.176*f - 0.7 ≤ ILD ≤ 0.176* f + 0.7 | 50MHz≤f ≤19GHz |
| Differential to common-mode Conversion Loss-Differential Insertion Loss(SCD21-SDD21) | Conversion _loss(f) – IL(f)≥ Where f is the frequency in GHz Conversion_loss(f ) is the cable assembly differential to common-mode conversion loss IL(f) is the cable assembly insertion loss | 10MHz≤f ≤19GHz |
| MDNEXT(multiple disturber near-end crosstalk) | ≥35dB @12.89GHz | 10MHz≤f ≤19GHz |
| Intra Skew | 15ps/m, | 10MHz≤f ≤19GHz |

2.2 其他电气性能

| 项目 | 需求 | 测试条件 |
| --- | --- | --- |
| Low Level Contact Resistance | 70milliohms Max. From initial. | EIA-364-23:Apply a maximum voltage of 20mV And a current of 100 mA. |
| Insulation Resistance | 10Mohm(Min.) | EIA364-21:AC 300V 1minute |
| Dielectric Withstanding Voltage | NO disruptive discharge. | EIA-364-20:Apply a voltage of 300 VDC for 1minute between adjacent terminals And between adjacent terminals and ground. |

2.3 环境表现

| 项目 | 需求 | 测试条件 |
| --- | --- | --- |
| Operating Temp. Range | -20°C to +75°C | Cable operating temperature range. |
| Storage Temp. Range (in packed condition) | -40°C to +80°C | Cable storage temperature range in packed condition. |
| Thermal Cycling Non-Powered | No evidence of physical damage | EIA-364-32D, Method A, -25 to 90C, 100 cycles, 15 min. dwells |
| Salt Spraying | 48 hours salt spraying after shell corrosive area less than 5％. | EIA-364-26 |
| Mixed Flowing Gas | Pass electrical tests per 3.1 after stressing. (For connector only) | EIA-364-35 Class II,14 days. |
| Temp. Life | No evidence of physical damage | EIA-364-17C w/ RH, Damp heat 90℃ at 85% RH for 500 hours then return to ambient |
| Cable Cold Bend | 4H,No evidence of physical damage | Condition: -20℃±2℃, mandrel diameter is 6 times the cable diameter. |

2.4 机械和物理特性

| 项目 | 需求 | 测试条件 |
| --- | --- | --- |
| Vibration | Pass electrical tests per 3.1 after stressing. | Clamp & vibrate per EIA-364-28E, TC-VII, test condition letter – D, 15 minutes in X, Y & Z axis. |
| Twist | No evidence of physical damage | Twist cable 180° (±90° from nominal position) for 100 cycles at 30 cycles per minute with a 0.5kg load applied to the cable jacket. Clamp position: 300mm |
| Cable Flex | No evidence of physical damage | Flex cable 180° for 20 cycles (±90° from nominal position) at 12 cycles per minute with a 1.0kg load applied to the cable jacket. Flex in the boot area 90º in each direction from vertical. Per EIA-364-41C |
| Cable Plug Retention in Cage | 90N Min. No evidence of physical damage | Force to be applied axially with no damage to cage. Per SFF 8661 Rev 2.1 Pull on cable jacket approximately 1 ft behind cable plug. No functional damage to cable plug below 90N. Per SFF-8432 Rev 5.0 |
| Cable Retention in Plug | 90N Min. No evidence of physical damage | Cable plug is fixtured with the bulk cable hanging vertically. A 90N axial load is applied (gradually) to the cable jacket and held for 1 minute. Per EIA-364-38B |
| Mechanical Shock | Pass electrical tests Per 3.1 after stressing. | Clamp and shock per EIA-364-27B, TC-G,3 times in 6 directions, 100g, 6ms. |
| Cable Plug Insertion | 40N Max.(QSFP28) | Per SFF8661 Rev 2.1 |
| Cable plug Extraction | 30N Max. (QSFP28) | Place axial load on de-latch to de-latch plug.Per SFF8661 Rev 2.1 |
| Durability | 50 cycles,No evidence of physical damage | EIA-364-09, perform plug &unplug cycles:Plug and receptacle mate rate: 250times/hour. 50times for QSFP28/SFP28 module (CONNECTOR TO PCB) |

- 简图:

两端的连接器用保护套保护，每个PC单独安装在防静电袋中。

<2m：200mm×300mm

2m：300mm *350mm

# Text boxes

16.5-2√f               0.05≤f﹤4.1

10.66-14log10(f/ 5.5)    4.1≤f≤19

22-(20/25.78)f   0.01≤f﹤12.89

15-(6/25.78)f    12.89≤f≤19

10              0.01≤f﹤12.89

27-(29/22)f     12.89≤f﹤15.7

6.3             15.7≤f≤19

300mm

350mm